## ورقة1
METER PARAMETER | BASIC SETTING | OPTIONS | OBIS | DESCRIPTION | ATTRIBUTES | R/W | RESULT | UNIT
|  |  | 1.0.0.6.3.255 | Maximum Current | 2 | R |  | A
|  |  | 1.0.0.3.0.255 | Meter constant for active energy, metrological LED | 2 | R |  | 1/(Wh)
|  |  | 1.0.0.4.2.255 | Transformer ratio - current (numerator) | 2 | R/W
|  |  | 1.0.0.4.5.255 | Transformer ratio - current (denominator) | 2 | R/W
|  |  | 0.0.96.1.0.255 | Device ID 1, manufacturing number | 2 | R/W
|  |  | 0.0.96.1.1.255 | Device ID | 2 | R/W
|  |  | 0.0.96.1.2.255 | Device model | 2 | R
|  |  | 0.0.96.1.3.255 | Hardware version | 2 | R
|  |  | 0.0.96.1.4.255 | Manufacture ID | 2 | R
|  |  | 0.0.96.1.5.255 | Production Date | 2 | R
|  |  | 0.0.42.0.0.255 | COSEM Logical device name | 2 | R
|  |  | 0.0.96.54.4.255 | Sunrise Time(HH:MM) | 2 | R
|  |  | 0.0.96.54.5.255 | Sunset Time(HH:MM) | 2 | R
|  |  | 0.0.96.54.6.255 | Longitude | 2 | R/W |  | °
|  |  | 0.0.96.54.7.255 | Latitude | 2 | R/W |  | °
|  |  | 1.0.0.2.0.255 | Active firmware version | 2 | R
|  |  | 1.0.0.2.0.255 | Communication Module firmware version | 2 | R
|  |  | 0.0.96.53.24.255 | Current over limit duration for disconnection | 2 | R/W |  | S
|  |  | 0.0.96.53.25.255 | Interval for reconnection after disconnection for current over limit | 2 | R/W |  | S
|  |  | 0.0.96.53.27.255 | Time to clear disconnection count | 2 | R/W |  | min
|  |  | 0.0.96.53.26.255 | Maximum reconnection for current over limit | 2 | R/W
|  |  | 1.0.33.32.0.255 | Number of voltage sags in phase L1 | 2 | R
|  |  | 1.0.53.32.0.255 | Number of voltage sags in phase L2 | 2 | R
|  |  | 1.0.73.32.0.255 | Number of voltage sags in phase L3 | 2 | R
|  |  | 1.0.33.36.0.255 | Number of voltage swells in phase L1 | 2 | R
|  |  | 1.0.53.36.0.255 | Number of voltage swells in phase L2 | 2 | R
|  |  | 1.0.73.36.0.255 | Number of voltage swells in phase L3 | 2 | R
|  | OPTIONS | OBIS | DESCRIPTION | RESULT
READ | INSTANTANEOUS VALUE |  | 1.0.14.7.0.255 | Supply frequency
|  |  | 1.0.32.7.0.255 | L1 Voltage
|  |  | 1.0.52.7.0.255 | L2 Voltage
|  |  | 1.0.72.7.0.255 | L3 Voltage
|  |  | 1.0.31.7.0.255 | L1 Current
|  |  | 1.0.51.7.0.255 | L2 Current
|  |  | 1.0.71.7.0.255 | L3 Current
|  |  | 1.0.90.7.0.255 | SLi current (algebraic sum of the currents in all phases)
|  |  | 1.0.2.7.0.255 | Sum Li Active power- (QII+QIII)
|  |  | 1.0.22.7.0.255 | L1 Active power- (QII+QIII)
|  |  | 1.0.42.7.0.255 | L2 Active power- (QII+QIII)
|  |  | 1.0.62.7.0.255 | L3 Active power- (QII+QIII)
|  |  | 1.0.1.7.0.255 | Sum Li Active power+ (QI+QIV)
|  |  | 1.0.21.7.0.255 | L1 Active power+ (QI+QIV)
|  |  | 1.0.41.7.0.255 | L2 Active power+ (QI+QIV)
|  |  | 1.0.61.7.0.255 | L3 Active power+ (QI+QIV)
|  |  | 1.0.3.7.0.255 | Sum Li Reactive power+ (QI+QII)
|  |  | 1.0.23.7.0.255 | L1 Reactive power+ (QI+QII)
|  |  | 1.0.43.7.0.255 | L2 Reactive power+ (QI+QII)
|  |  | 1.0.63.7.0.255 | L3 Reactive power+ (QI+QII)
|  |  | 1.0.4.7.0.255 | Sum Li Reactive power- (QIII+QIV)
|  |  | 1.0.24.7.0.255 | L1 Reactive power- (QIII+QIV)
|  |  | 1.0.44.7.0.255 | L2 Reactive power- (QIII+QIV)
|  |  | 1.0.64.7.0.255 | L3 Reactive power- (QIII+QIV)
|  |  | 1.0.9.7.0.255 | Sum Li Apparent power+ (QI+QIV)
|  |  | 1.0.29.7.0.255 | L1 Apparent power+ (QI+QIV)
|  |  | 1.0.49.7.0.255 | L2 Apparent power+ (QI+QIV)
|  |  | 1.0.69.7.0.255 | L3 Apparent power+ (QI+QIV)
|  |  | 1.0.10.7.0.255 | Sum Li Apparent power- (QII+QIII)
|  |  | 1.0.30.7.0.255 | L1 Apparent power- (QII+QIII)
|  |  | 1.0.50.7.0.255 | L2 Apparent power- (QII+QIII)
|  |  | 1.0.70.7.0.255 | L3 Apparent power- (QII+QIII)
|  |  | 1.0.13.7.0.255 | Sum Li Power factor
|  |  | 1.0.33.7.0.255 | L1 Power factor
|  |  | 1.0.53.7.0.255 | L2 Power factor
|  |  | 1.0.73.7.0.255 | L3 Power factor
|  |  | 1.0.81.7.10.255 | Angle of U(L1) - U(L2)
|  |  | 1.0.81.7.20.255 | Angle of U(L1) - U(L3)
|  |  | 1.0.81.7.40.255 | Angle of U(L1) - I(L1)
|  |  | 1.0.81.7.51.255 | Angle of U(L2) - I(L2)
|  |  | 1.0.81.7.62.255 | Angle of U(L3) - I(L3)
|  |  | 1.0.91.7.0.255 | Lo Current (neutral)
|  |  | 0.0.96.6.3.255 | Battery voltage
|  | OPTIONS | OBIS | DESCRIPTION | RESULT
| MAXIMUM MDI |  | 1.0.1.6.0.255 | Demand value - active power+ (QI+QIV)
|  |  | 1.0.1.6.0.255 | Demand time - active power+ (QI+QIV)
|  |  | 1.0.1.6.t.255 | Demand value - active power+ (QI+QIV), TOU Register
|  |  | 1.0.1.6.1.255 | Demand value - active power+ (QI+QIV) of T1
|  |  | 1.0.1.6.2.255 | Demand value - active power+ (QI+QIV) of T2
|  |  | 1.0.1.6.3.255 | Demand value - active power+ (QI+QIV) of T3
|  |  | 1.0.1.6.4.255 | Demand value - active power+ (QI+QIV) of T4
|  |  | 1.0.1.6.t.255 | Demand time - active power+ (QI+QIV), TOU Register
|  |  | 1.0.1.6.1.255 | Demand time - active power+ (QI+QIV) of T1
|  |  | 1.0.1.6.2.255 | Demand time - active power+ (QI+QIV) of T2
|  |  | 1.0.1.6.3.255 | Demand time - active power+ (QI+QIV) of T3
|  |  | 1.0.1.6.4.255 | Demand time - active power+ (QI+QIV) of T4
|  |  | 1.0.2.6.0.255 | Demand value - active power– (QII+QIII)
|  |  | 1.0.2.6.0.255 | Demand time - active power– (QII+QIII)
|  |  | 1.0.2.6.t.255 | Demand value - active power– (QII+QIII), TOU Register
|  |  | 1.0.2.6.1.255 | Demand value - active power– (QII+QIII) of T1
|  |  | 1.0.2.6.2.255 | Demand value - active power– (QII+QIII) of T2
|  |  | 1.0.2.6.3.255 | Demand value - active power– (QII+QIII) of T3
|  |  | 1.0.2.6.4.255 | Demand value - active power– (QII+QIII) of T4
|  |  | 1.0.2.6.t.255 | Demand time - active power– (QII+QIII), TOU Register
|  |  | 1.0.2.6.1.255 | Demand time - active power– (QII+QIII) of T1
|  |  | 1.0.2.6.2.255 | Demand time - active power– (QII+QIII) of T2
|  |  | 1.0.2.6.3.255 | Demand time - active power– (QII+QIII) of T3
|  |  | 1.0.2.6.4.255 | Demand time - active power– (QII+QIII) of T4
|  |  | 1.0.3.6.0.255 | Demand value - reactive power+ (QI+QII)
|  |  | 1.0.3.6.0.255 | Demand time - reactive power+ (QI+QII)
|  |  | 1.0.3.6.t.255 | Demand value - reactive power+ (QI+QII), TOU Register
|  |  | 1.0.3.6.1.255 | Demand value - reactive power+ (QI+QII) of T1
|  |  | 1.0.3.6.2.255 | Demand value - reactive power+ (QI+QII) of T2
|  |  | 1.0.3.6.3.255 | Demand value - reactive power+ (QI+QII) of T3
|  |  | 1.0.3.6.4.255 | Demand value - reactive power+ (QI+QII) of T4
|  |  | 1.0.3.6.t.255 | Demand time - reactive power+ (QI+QII), TOU Register
|  |  | 1.0.3.6.1.255 | Demand time - reactive power+ (QI+QII) of T1
|  |  | 1.0.3.6.2.255 | Demand time - reactive power+ (QI+QII) of T2
|  |  | 1.0.3.6.3.255 | Demand time - reactive power+ (QI+QII) of T3
|  |  | 1.0.3.6.4.255 | Demand time - reactive power+ (QI+QII) of T4
|  |  | 1.0.4.6.0.255 | Demand value - reactive power– (QIII+QIV)
|  |  | 1.0.4.6.0.255 | Demand time - reactive power– (QIII+QIV)
|  |  | 1.0.4.6.t.255 | Demand value - reactive power– (QIII+QIV), TOU Register
|  |  | 1.0.4.6.1.255 | Demand value - reactive power– (QIII+QIV) of T1
|  |  | 1.0.4.6.2.255 | Demand value - reactive power– (QIII+QIV) of T2
|  |  | 1.0.4.6.3.255 | Demand value - reactive power– (QIII+QIV) of T3
|  |  | 1.0.4.6.4.255 | Demand value - reactive power– (QIII+QIV) of T4
|  |  | 1.0.4.6.t.255 | Demand time - reactive power– (QIII+QIV), TOU Register
|  |  | 1.0.4.6.1.255 | Demand time - reactive power– (QIII+QIV) of T1
|  |  | 1.0.4.6.2.255 | Demand time - reactive power– (QIII+QIV) of T2
|  |  | 1.0.4.6.3.255 | Demand time - reactive power– (QIII+QIV) of T3
|  |  | 1.0.4.6.4.255 | Demand time - reactive power– (QIII+QIV) of T4
|  |  | 1.0.9.6.0.255 | Demand value - apparent power+ (QI+QIV)
|  |  | 1.0.9.6.0.255 | Demand time - apparent power+ (QI+QIV)
|  |  | 1.0.9.6.t.255 | Demand value - apparent power+ (QI+QIV), TOU Register
|  |  | 1.0.9.6.1.255 | Demand value - apparent power+ (QI+QIV) of T1
|  |  | 1.0.9.6.2.255 | Demand value - apparent power+ (QI+QIV) of T2
|  |  | 1.0.9.6.3.255 | Demand value - apparent power+ (QI+QIV) of T3
|  |  | 1.0.9.6.4.255 | Demand value - apparent power+ (QI+QIV) of T4
|  |  | 1.0.9.6.t.255 | Demand time - apparent power+ (QI+QIV), TOU Register
|  |  | 1.0.9.6.1.255 | Demand time - apparent power+ (QI+QIV) of T1
|  |  | 1.0.9.6.2.255 | Demand time - apparent power+ (QI+QIV) of T2
|  |  | 1.0.9.6.3.255 | Demand time - apparent power+ (QI+QIV) of T3
|  |  | 1.0.9.6.4.255 | Demand time - apparent power+ (QI+QIV) of T4
|  |  | 1.0.10.6.0.255 | Demand value - apparent power– (QII+QIII)
|  |  | 1.0.10.6.0.255 | Demand time - apparent power– (QII+QIII)
|  |  | 1.0.10.6.t.255 | Demand value - apparent power– (QII+QIII), TOU Register
|  |  | 1.0.10.6.1.255 | Demand value - apparent power– (QII+QIII) of T1
|  |  | 1.0.10.6.2.255 | Demand value - apparent power– (QII+QIII) of T2
|  |  | 1.0.10.6.3.255 | Demand value - apparent power– (QII+QIII) of T3
|  |  | 1.0.10.6.4.255 | Demand value - apparent power– (QII+QIII) of T4
|  |  | 1.0.10.6.t.255 | Demand time - apparent power– (QII+QIII), TOU Register
|  |  | 1.0.10.6.1.255 | Demand time - apparent power– (QII+QIII) of T1
|  |  | 1.0.10.6.2.255 | Demand time - apparent power– (QII+QIII) of T2
|  |  | 1.0.10.6.3.255 | Demand time - apparent power– (QII+QIII) of T3
|  |  | 1.0.10.6.4.255 | Demand time - apparent power– (QII+QIII) of T4
|  |  | 1.0.15.6.0.255 | Demand value - active power (abs(QI+QIV)+(abs(QII+QIII))
|  |  | 1.0.15.6.0.255 | Demand time - active power (abs(QI+QIV)+(abs(QII+QIII))
|  |  | 1.0.15.6.t.255 | Demand value - active power (abs(QI+QIV)+(abs(QII+QIII)), TOU Register
|  |  | 1.0.15.6.1.255 | Demand value - active power (abs(QI+QIV)+(abs(QII+QIII)) of T1
|  |  | 1.0.15.6.2.255 | Demand value - active power (abs(QI+QIV)+(abs(QII+QIII)) of T2
|  |  | 1.0.15.6.3.255 | Demand value - active power (abs(QI+QIV)+(abs(QII+QIII)) of T3
|  |  | 1.0.15.6.4.255 | Demand value - active power (abs(QI+QIV)+(abs(QII+QIII)) of T4
|  |  | 1.0.15.6.t.255 | Demand time - active power (abs(QI+QIV)+(abs(QII+QIII)), TOU Register
|  |  | 1.0.15.6.1.255 | Demand time - active power (abs(QI+QIV)+(abs(QII+QIII)) of T1
|  |  | 1.0.15.6.2.255 | Demand time - active power (abs(QI+QIV)+(abs(QII+QIII)) of T2
|  |  | 1.0.15.6.3.255 | Demand time - active power (abs(QI+QIV)+(abs(QII+QIII)) of T3
|  |  | 1.0.15.6.4.255 | Demand time - active power (abs(QI+QIV)+(abs(QII+QIII)) of T4
|  | OPTIONS | OBIS | DESCRIPTION | RESULT
| ENERGY REGISTER |  | 1.0.1.8.0.255 | Cumulative active energy+ (QI+QIV)
|  |  | 1.0.1.8.t.255 | Cumulative active energy+ (QI+QIV), TOU Register
|  |  | 1.0.1.8.1.255 | Cumulative active energy+ (QI+QIV) of T1
|  |  | 1.0.1.8.2.255 | Cumulative active energy+ (QI+QIV) of T2
|  |  | 1.0.1.8.3.255 | Cumulative active energy+ (QI+QIV) of T3
|  |  | 1.0.1.8.4.255 | Cumulative active energy+ (QI+QIV) of T4
|  |  | 1.0.2.8.0.255 | Cumulative active energy– (QII+QIII)
|  |  | 1.0.2.8.t.255 | Cumulative active energy– (QII+QIII), TOU Register
|  |  | 1.0.2.8.1.255 | Cumulative active energy– (QII+QIII) of T1
|  |  | 1.0.2.8.2.255 | Cumulative active energy– (QII+QIII) of T2
|  |  | 1.0.2.8.3.255 | Cumulative active energy– (QII+QIII) of T3
|  |  | 1.0.2.8.4.255 | Cumulative active energy– (QII+QIII) of T4
|  |  | 1.0.3.8.0.255 | Cumulative reactive energy+ (QI+QII)
|  |  | 1.0.3.8.t.255 | Cumulative reactive energy+ (QI+QII), TOU Register
|  |  | 1.0.3.8.1.255 | Cumulative reactive energy+ (QI+QII) of T1
|  |  | 1.0.3.8.2.255 | Cumulative reactive energy+ (QI+QII) of T2
|  |  | 1.0.3.8.3.255 | Cumulative reactive energy+ (QI+QII) of T3
|  |  | 1.0.3.8.4.255 | Cumulative reactive energy+ (QI+QII) of T4
|  |  | 1.0.4.8.0.255 | Cumulative reactive energy– (QIII+QIV)
|  |  | 1.0.4.8.t.255 | Cumulative reactive energy– (QIII+QIV), TOU Register
|  |  | 1.0.4.8.1.255 | Cumulative reactive energy– (QIII+QIV) of T1
|  |  | 1.0.4.8.2.255 | Cumulative reactive energy– (QIII+QIV) of T2
|  |  | 1.0.4.8.3.255 | Cumulative reactive energy– (QIII+QIV) of T3
|  |  | 1.0.4.8.4.255 | Cumulative reactive energy– (QIII+QIV) of T4
|  |  | 1.0.5.8.0.255 | Cumulative reactive energy QI
|  |  | 1.0.5.8.t.255 | Cumulative reactive energy QI, TOU Register
|  |  | 1.0.5.8.1.255 | Cumulative reactive energy QI of T1
|  |  | 1.0.5.8.2.255 | Cumulative reactive energy QI of T2
|  |  | 1.0.5.8.3.255 | Cumulative reactive energy QI of T3
|  |  | 1.0.5.8.4.255 | Cumulative reactive energy QI of T4
|  |  | 1.0.6.8.0.255 | Cumulative reactive energy QII
|  |  | 1.0.6.8.t.255 | Cumulative reactive energy QII, TOU Register
|  |  | 1.0.6.8.1.255 | Cumulative reactive energy QII of T1
|  |  | 1.0.6.8.2.255 | Cumulative reactive energy QII of T2
|  |  | 1.0.6.8.3.255 | Cumulative reactive energy QII of T3
|  |  | 1.0.6.8.4.255 | Cumulative reactive energy QII of T4
|  |  | 1.0.7.8.0.255 | Cumulative reactive energy QIII
|  |  | 1.0.7.8.t.255 | Cumulative reactive energy QIII, TOU Register
|  |  | 1.0.7.8.1.255 | Cumulative reactive energy QIII of T1
|  |  | 1.0.7.8.2.255 | Cumulative reactive energy QIII of T2
|  |  | 1.0.7.8.3.255 | Cumulative reactive energy QIII of T3
|  |  | 1.0.7.8.4.255 | Cumulative reactive energy QIII of T4
|  |  | 1.0.8.8.0.255 | Cumulative reactive energy QIV
|  |  | 1.0.8.8.t.255 | Cumulative reactive energy QIV, TOU Register
|  |  | 1.0.8.8.1.255 | Cumulative reactive energy QIV of T1
|  |  | 1.0.8.8.2.255 | Cumulative reactive energy QIV of T2
|  |  | 1.0.8.8.3.255 | Cumulative reactive energy QIV of T3
|  |  | 1.0.8.8.4.255 | Cumulative reactive energy QIV of T4
|  |  | 1.0.9.8.0.255 | Cumulative apparent energy+ (QI+QIV)
|  |  | 1.0.9.8.t.255 | Cumulative apparent energy+ (QI+QIV), TOU Register
|  |  | 1.0.9.8.1.255 | Cumulative apparent energy+ (QI+QIV) of T1
|  |  | 1.0.9.8.2.255 | Cumulative apparent energy+ (QI+QIV) of T2
|  |  | 1.0.9.8.3.255 | Cumulative apparent energy+ (QI+QIV) of T3
|  |  | 1.0.9.8.4.255 | Cumulative apparent energy+ (QI+QIV) of T4
|  |  | 1.0.10.8.0.255 | Cumulative apparent energy– (QII+QIII)
|  |  | 1.0.10.8.t.255 | Cumulative apparent energy– (QII+QIII), TOU Register
|  |  | 1.0.10.8.1.255 | Cumulative apparent energy– (QII+QIII) of T1
|  |  | 1.0.10.8.2.255 | Cumulative apparent energy– (QII+QIII) of T2
|  |  | 1.0.10.8.3.255 | Cumulative apparent energy– (QII+QIII) of T3
|  |  | 1.0.10.8.4.255 | Cumulative apparent energy– (QII+QIII) of T4
|  |  | 1.0.15.8.0.255 | Cumulative active energy (abs(QI+QIV)+(abs(QII+QIII))
|  |  | 1.0.15.8.t.255 | Cumulative active energy (abs(QI+QIV)+(abs(QII+QIII)), TOU Register
|  |  | 1.0.15.8.1.255 | Cumulative active energy (abs(QI+QIV)+(abs(QII+QIII)) of T1
|  |  | 1.0.15.8.2.255 | Cumulative active energy (abs(QI+QIV)+(abs(QII+QIII)) of T2
|  |  | 1.0.15.8.3.255 | Cumulative active energy (abs(QI+QIV)+(abs(QII+QIII)) of T3
|  |  | 1.0.15.8.4.255 | Cumulative active energy (abs(QI+QIV)+(abs(QII+QIII)) of T4
|  | OPTIONS | OBIS | DESCRIPTION | RESULT
| CURRENT MDU |  | 1.0.1.4.0.255 | Demand value - average active power+ (QI+QIV)
|  |  | 1.0.1.4.0.255 | Demand time - average active power+ (QI+QIV)
|  |  | 1.0.2.4.0.255 | Demand value - average active power– (QII+QIII)
|  |  | 1.0.2.4.0.255 | Demand time - average active power– (QII+QIII)
|  |  | 1.0.3.4.0.255 | Demand value - average reactive power+ (QI+QII)
|  |  | 1.0.3.4.0.255 | Demand time - average reactive power+ (QI+QII)
|  |  | 1.0.4.4.0.255 | Demand value - average reactive power– (QIII+QIV)
|  |  | 1.0.4.4.0.255 | Demand time - average reactive power– (QIII+QIV)
|  |  | 1.0.9.4.0.255 | Demand value - average apparent power+ (QI+QIV)
|  |  | 1.0.9.4.0.255 | Demand time - average apparent power+ (QI+QIV)
|  |  | 1.0.10.4.0.255 | Demand value - average apparent power– (QII+QIII)
|  |  | 1.0.10.4.0.255 | Demand time - average apparent power– (QII+QIII)
|  |  | 1.0.15.4.0.255 | Demand time - average active power (abs(QI+QIV)+(abs(QII+QIII))
|  | OPTIONS | OBIS | DESCRIPTION | RESULT
| HISTORY ENERGY |  | 1.0.1.8.0.n | Cumulative active energy+ (QI+QIV) of last n billing period
|  |  | 1.0.1.8.0.101 | Cumulative active energy+ (QI+QIV) of last 1 billing period
|  |  | 1.0.1.8.0.102 | Cumulative active energy+ (QI+QIV) of last 2 billing period
|  |  | 1.0.1.8.0.103 | Cumulative active energy+ (QI+QIV) of last 3 billing period
|  |  | 1.0.1.8.0.104 | Cumulative active energy+ (QI+QIV) of last 4 billing period
|  |  | 1.0.1.8.0.105 | Cumulative active energy+ (QI+QIV) of last 5 billing period
|  |  | 1.0.1.8.0.106 | Cumulative active energy+ (QI+QIV) of last 6 billing period
|  |  | 1.0.1.8.0.107 | Cumulative active energy+ (QI+QIV) of last 7 billing period
|  |  | 1.0.1.8.0.108 | Cumulative active energy+ (QI+QIV) of last 8 billing period
|  |  | 1.0.1.8.0.109 | Cumulative active energy+ (QI+QIV) of last 9 billing period
|  |  | 1.0.1.8.0.110 | Cumulative active energy+ (QI+QIV) of last 10 billing period
|  |  | 1.0.1.8.0.111 | Cumulative active energy+ (QI+QIV) of last 11 billing period
|  |  | 1.0.1.8.t.n | Cumulative active energy+ (QI+QIV), TOU Register of last n billing period
|  |  | 1.0.1.8.1.101 | Cumulative active energy+ (QI+QIV) of T1 of last 1 billing period
|  |  | 1.0.1.8.1.102 | Cumulative active energy+ (QI+QIV) of T1 of last 2 billing period
|  |  | 1.0.1.8.1.103 | Cumulative active energy+ (QI+QIV) of T1 of last 3 billing period
|  |  | 1.0.1.8.1.104 | Cumulative active energy+ (QI+QIV) of T1 of last 4 billing period
|  |  | 1.0.1.8.1.105 | Cumulative active energy+ (QI+QIV) of T1 of last 5 billing period
|  |  | 1.0.1.8.1.106 | Cumulative active energy+ (QI+QIV) of T1 of last 6 billing period
|  |  | 1.0.1.8.1.107 | Cumulative active energy+ (QI+QIV) of T1 of last 7 billing period
|  |  | 1.0.1.8.1.108 | Cumulative active energy+ (QI+QIV) of T1 of last 8 billing period
|  |  | 1.0.1.8.1.109 | Cumulative active energy+ (QI+QIV) of T1 of last 9 billing period
|  |  | 1.0.1.8.1.110 | Cumulative active energy+ (QI+QIV) of T1 of last 10 billing period
|  |  | 1.0.1.8.1.111 | Cumulative active energy+ (QI+QIV) of T1 of last 11 billing period
|  |  | 1.0.1.8.1.112 | Cumulative active energy+ (QI+QIV) of T1 of last 12 billing period
|  |  | 1.0.1.8.2.101 | Cumulative active energy+ (QI+QIV) of T2 of last 1 billing period
|  |  | 1.0.1.8.2.102 | Cumulative active energy+ (QI+QIV) of T2 of last 2 billing period
|  |  | 1.0.1.8.2.103 | Cumulative active energy+ (QI+QIV) of T2 of last 3 billing period
|  |  | 1.0.1.8.2.104 | Cumulative active energy+ (QI+QIV) of T2 of last 4 billing period
|  |  | 1.0.1.8.2.105 | Cumulative active energy+ (QI+QIV) of T2 of last 5 billing period
|  |  | 1.0.1.8.2.106 | Cumulative active energy+ (QI+QIV) of T2 of last 6 billing period
|  |  | 1.0.1.8.2.107 | Cumulative active energy+ (QI+QIV) of T2 of last 7 billing period
|  |  | 1.0.1.8.2.108 | Cumulative active energy+ (QI+QIV) of T2 of last 8 billing period
|  |  | 1.0.1.8.2.109 | Cumulative active energy+ (QI+QIV) of T2 of last 9 billing period
|  |  | 1.0.1.8.2.110 | Cumulative active energy+ (QI+QIV) of T2 of last 10 billing period
|  |  | 1.0.1.8.2.111 | Cumulative active energy+ (QI+QIV) of T2 of last 11 billing period
|  |  | 1.0.1.8.2.112 | Cumulative active energy+ (QI+QIV) of T2 of last 12 billing period
|  |  | 1.0.1.8.3.101 | Cumulative active energy+ (QI+QIV) of T3 of last 1 billing period
|  |  | 1.0.1.8.3.102 | Cumulative active energy+ (QI+QIV) of T3 of last 2 billing period
|  |  | 1.0.1.8.3.103 | Cumulative active energy+ (QI+QIV) of T3 of last 3 billing period
|  |  | 1.0.1.8.3.104 | Cumulative active energy+ (QI+QIV) of T3 of last 4 billing period
|  |  | 1.0.1.8.3.105 | Cumulative active energy+ (QI+QIV) of T3 of last 5 billing period
|  |  | 1.0.1.8.3.106 | Cumulative active energy+ (QI+QIV) of T3 of last 6 billing period
|  |  | 1.0.1.8.3.107 | Cumulative active energy+ (QI+QIV) of T3 of last 7 billing period
|  |  | 1.0.1.8.3.108 | Cumulative active energy+ (QI+QIV) of T3 of last 8 billing period
|  |  | 1.0.1.8.3.109 | Cumulative active energy+ (QI+QIV) of T3 of last 9 billing period
|  |  | 1.0.1.8.3.110 | Cumulative active energy+ (QI+QIV) of T3 of last 10 billing period
|  |  | 1.0.1.8.3.111 | Cumulative active energy+ (QI+QIV) of T3 of last 11 billing period
|  |  | 1.0.1.8.3.112 | Cumulative active energy+ (QI+QIV) of T3 of last 12 billing period
|  |  | 1.0.1.8.4.101 | Cumulative active energy+ (QI+QIV) of T4 of last 1 billing period
|  |  | 1.0.1.8.4.102 | Cumulative active energy+ (QI+QIV) of T4 of last 2 billing period
|  |  | 1.0.1.8.4.103 | Cumulative active energy+ (QI+QIV) of T4 of last 3 billing period
|  |  | 1.0.1.8.4.104 | Cumulative active energy+ (QI+QIV) of T4 of last 4 billing period
|  |  | 1.0.1.8.4.105 | Cumulative active energy+ (QI+QIV) of T4 of last 5 billing period
|  |  | 1.0.1.8.4.106 | Cumulative active energy+ (QI+QIV) of T4 of last 6 billing period
|  |  | 1.0.1.8.4.107 | Cumulative active energy+ (QI+QIV) of T4 of last 7 billing period
|  |  | 1.0.1.8.4.108 | Cumulative active energy+ (QI+QIV) of T4 of last 8 billing period
|  |  | 1.0.1.8.4.109 | Cumulative active energy+ (QI+QIV) of T4 of last 9 billing period
|  |  | 1.0.1.8.4.110 | Cumulative active energy+ (QI+QIV) of T4 of last 10 billing period
|  |  | 1.0.1.8.4.111 | Cumulative active energy+ (QI+QIV) of T4 of last 11 billing period
|  |  | 1.0.1.8.4.112 | Cumulative active energy+ (QI+QIV) of T4 of last 12 billing period
|  |  | 1.0.2.8.0.n | Cumulative active energy– (QII+QIII) of last n billing period
|  |  | 1.0.2.8.0.101 | Cumulative active energy– (QII+QIII) of last 1 billing period
|  |  | 1.0.2.8.0.102 | Cumulative active energy– (QII+QIII) of last 2 billing period
|  |  | 1.0.2.8.0.103 | Cumulative active energy– (QII+QIII) of last 3 billing period
|  |  | 1.0.2.8.0.104 | Cumulative active energy– (QII+QIII) of last 4 billing period
|  |  | 1.0.2.8.0.105 | Cumulative active energy– (QII+QIII) of last 5 billing period
|  |  | 1.0.2.8.0.106 | Cumulative active energy– (QII+QIII) of last 6 billing period
|  |  | 1.0.2.8.0.107 | Cumulative active energy– (QII+QIII) of last 7 billing period
|  |  | 1.0.2.8.0.108 | Cumulative active energy– (QII+QIII) of last 8 billing period
|  |  | 1.0.2.8.0.109 | Cumulative active energy– (QII+QIII) of last 9 billing period
|  |  | 1.0.2.8.0.110 | Cumulative active energy– (QII+QIII) of last 10 billing period
|  |  | 1.0.2.8.0.111 | Cumulative active energy– (QII+QIII) of last 11 billing period
|  |  | 1.0.2.8.0.112 | Cumulative active energy– (QII+QIII) of last 12 billing period
|  |  | 1.0.2.8.t.n | Cumulative active energy– (QII+QIII), TOU Register of last n billing period
|  |  | 1.0.2.8.1.101 | Cumulative active energy– (QII+QIII) of T1 of last 1 billing period
|  |  | 1.0.2.8.1.102 | Cumulative active energy– (QII+QIII) of T1 of last 2 billing period
|  |  | 1.0.2.8.1.103 | Cumulative active energy– (QII+QIII) of T1 of last 3 billing period
|  |  | 1.0.2.8.1.104 | Cumulative active energy– (QII+QIII) of T1 of last 4 billing period
|  |  | 1.0.2.8.1.105 | Cumulative active energy– (QII+QIII) of T1 of last 5 billing period
|  |  | 1.0.2.8.1.106 | Cumulative active energy– (QII+QIII) of T1 of last 6 billing period
|  |  | 1.0.2.8.1.107 | Cumulative active energy– (QII+QIII) of T1 of last 7 billing period
|  |  | 1.0.2.8.1.108 | Cumulative active energy– (QII+QIII) of T1 of last 8 billing period
|  |  | 1.0.2.8.1.109 | Cumulative active energy– (QII+QIII) of T1 of last 9 billing period
|  |  | 1.0.2.8.1.110 | Cumulative active energy– (QII+QIII) of T1 of last 10 billing period
|  |  | 1.0.2.8.1.111 | Cumulative active energy– (QII+QIII) of T1 of last 11 billing period
|  |  | 1.0.2.8.1.112 | Cumulative active energy– (QII+QIII) of T1 of last 12 billing period
|  |  | 1.0.2.8.2.101 | Cumulative active energy– (QII+QIII) of T2 of last 1 billing period
|  |  | 1.0.2.8.2.102 | Cumulative active energy– (QII+QIII) of T2 of last 2 billing period
|  |  | 1.0.2.8.2.103 | Cumulative active energy– (QII+QIII) of T2 of last 3 billing period
|  |  | 1.0.2.8.2.104 | Cumulative active energy– (QII+QIII) of T2 of last 4 billing period
|  |  | 1.0.2.8.2.105 | Cumulative active energy– (QII+QIII) of T2 of last 5 billing period
|  |  | 1.0.2.8.2.106 | Cumulative active energy– (QII+QIII) of T2 of last 6 billing period
|  |  | 1.0.2.8.2.107 | Cumulative active energy– (QII+QIII) of T2 of last 7 billing period
|  |  | 1.0.2.8.2.108 | Cumulative active energy– (QII+QIII) of T2 of last 8 billing period
|  |  | 1.0.2.8.2.109 | Cumulative active energy– (QII+QIII) of T2 of last 9 billing period
|  |  | 1.0.2.8.2.110 | Cumulative active energy– (QII+QIII) of T2 of last 10 billing period
|  |  | 1.0.2.8.2.111 | Cumulative active energy– (QII+QIII) of T2 of last 11 billing period
|  |  | 1.0.2.8.2.112 | Cumulative active energy– (QII+QIII) of T2 of last 12 billing period
|  |  | 1.0.2.8.3.101 | Cumulative active energy– (QII+QIII) of T3 of last 1 billing period
|  |  | 1.0.2.8.3.102 | Cumulative active energy– (QII+QIII) of T3 of last 2 billing period
|  |  | 1.0.2.8.3.103 | Cumulative active energy– (QII+QIII) of T3 of last 3 billing period
|  |  | 1.0.2.8.3.104 | Cumulative active energy– (QII+QIII) of T3 of last 4 billing period
|  |  | 1.0.2.8.3.105 | Cumulative active energy– (QII+QIII) of T3 of last 5 billing period
|  |  | 1.0.2.8.3.106 | Cumulative active energy– (QII+QIII) of T3 of last 6 billing period
|  |  | 1.0.2.8.3.107 | Cumulative active energy– (QII+QIII) of T3 of last 7 billing period
|  |  | 1.0.2.8.3.108 | Cumulative active energy– (QII+QIII) of T3 of last 8 billing period
|  |  | 1.0.2.8.3.109 | Cumulative active energy– (QII+QIII) of T3 of last 9 billing period
|  |  | 1.0.2.8.3.110 | Cumulative active energy– (QII+QIII) of T3 of last 10 billing period
|  |  | 1.0.2.8.3.111 | Cumulative active energy– (QII+QIII) of T3 of last 11 billing period
|  |  | 1.0.2.8.3.112 | Cumulative active energy– (QII+QIII) of T3 of last 12 billing period
|  | OPTIONS | OBIS | DESCRIPTION | RESULT
| BILING PERIOD ENERGY |  | 1.0.15.9.0.255 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII))
|  |  | 1.0.15.9.0.n | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of last n billing period
|  |  | 1.0.15.9.0.101 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of last 1 billing period
|  |  | 1.0.15.9.0.102 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of last 2 billing period
|  |  | 1.0.15.9.0.103 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of last 3 billing period
|  |  | 1.0.15.9.0.104 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of last 4 billing period
|  |  | 1.0.15.9.0.105 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of last 5 billing period
|  |  | 1.0.15.9.0.106 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of last 6 billing period
|  |  | 1.0.15.9.0.107 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of last 7 billing period
|  |  | 1.0.15.9.0.108 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of last 8 billing period
|  |  | 1.0.15.9.0.109 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of last 9 billing period
|  |  | 1.0.15.9.0.110 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of last 10 billing period
|  |  | 1.0.15.9.0.111 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of last 11 billing period
|  |  | 1.0.15.9.0.112 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of last 12 billing period
|  |  | 1.0.15.9.t.255 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)), TOU Register
|  |  | 1.0.15.9.1.255 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T1
|  |  | 1.0.15.9.1.255 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T2
|  |  | 1.0.15.9.3.255 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T3
|  |  | 1.0.15.9.4.255 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T4
|  |  | 1.0.15.9.t.n | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)), TOU Register of last n billing period
|  |  | 1.0.15.9.1.101 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T1 of last 1 billing period
|  |  | 1.0.15.9.1.102 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T1 of last 2 billing period
|  |  | 1.0.15.9.1.103 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T1 of last 3 billing period
|  |  | 1.0.15.9.1.104 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T1 of last 4 billing period
|  |  | 1.0.15.9.1.105 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T1 of last 5 billing period
|  |  | 1.0.15.9.1.106 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T1 of last 6 billing period
|  |  | 1.0.15.9.1.107 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T1 of last 7 billing period
|  |  | 1.0.15.9.1.108 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T1 of last 8 billing period
|  |  | 1.0.15.9.1.109 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T1 of last 9 billing period
|  |  | 1.0.15.9.1.110 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T1 of last 10 billing period
|  |  | 1.0.15.9.1.111 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T1 of last 11 billing period
|  |  | 1.0.15.9.1.112 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T1 of last 12 billing period
|  |  | 1.0.15.9.2.101 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T2 of last 1 billing period
|  |  | 1.0.15.9.2.102 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T2 of last 2 billing period
|  |  | 1.0.15.9.2.103 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T2 of last 3 billing period
|  |  | 1.0.15.9.2.104 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T2 of last 4 billing period
|  |  | 1.0.15.9.2.105 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T2 of last 5 billing period
|  |  | 1.0.15.9.2.106 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T2 of last 6 billing period
|  |  | 1.0.15.9.2.107 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T2 of last 7 billing period
|  |  | 1.0.15.9.2.108 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T2 of last 8 billing period
|  |  | 1.0.15.9.2.109 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T2 of last 9 billing period
|  |  | 1.0.15.9.2.110 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T2 of last 10 billing period
|  |  | 1.0.15.9.2.111 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T2 of last 11 billing period
|  |  | 1.0.15.9.2.112 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T2 of last 12 billing period
|  |  | 1.0.15.9.3.101 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T3 of last 1 billing period
|  |  | 1.0.15.9.3.102 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T3 of last 2 billing period
|  |  | 1.0.15.9.3.103 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T3 of last 3 billing period
|  |  | 1.0.15.9.3.104 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T3 of last 4 billing period
|  |  | 1.0.15.9.3.105 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T3 of last 5 billing period
|  |  | 1.0.15.9.3.106 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T3 of last 6 billing period
|  |  | 1.0.15.9.3.107 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T3 of last 7 billing period
|  |  | 1.0.15.9.3.108 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T3 of last 8 billing period
|  |  | 1.0.15.9.3.109 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T3 of last 9 billing period
|  |  | 1.0.15.9.3.110 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T3 of last 10 billing period
|  |  | 1.0.15.9.3.111 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T3 of last 11 billing period
|  |  | 1.0.15.9.3.112 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T3 of last 12 billing period
|  |  | 1.0.15.9.4.101 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T4 of last 1 billing period
|  |  | 1.0.15.9.4.102 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T4 of last 2 billing period
|  |  | 1.0.15.9.4.103 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T4 of last 3 billing period
|  |  | 1.0.15.9.4.104 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T4 of last 4 billing period
|  |  | 1.0.15.9.4.105 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T4 of last 5 billing period
|  |  | 1.0.15.9.4.106 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T4 of last 6 billing period
|  |  | 1.0.15.9.4.107 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T4 of last 7 billing period
|  |  | 1.0.15.9.4.108 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T4 of last 8 billing period
|  |  | 1.0.15.9.4.109 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T4 of last 9 billing period
|  |  | 1.0.15.9.4.110 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T4 of last 10 billing period
|  |  | 1.0.15.9.4.111 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T4 of last 11 billing period
|  |  | 1.0.15.9.4.112 | Billing period active energy (abs(QI+QIV)+(abs(QII+QIII)) of T4 of last 12 billing period